Here are the next steps in order, to pick up whenever you’re ready. Each one is a short session.

A. Finish the ETAP study (roadmap item 3)

- Stage 2: short circuit.

  - First a 3-phase fault with only the grid connected, at Bus-COMM, H11 and H22. The hand-check values are 1595 A, 713 A and 552 A.

  - Then the island case, where the inverter supplies the fault current. I estimate about 31 A, which is below the 40 A node trip. That’s a real protection question: in the island, would a fault ever trip the node?

- Stage 3: harmonics. Add a harmonic source for the inverters and check voltage THD against IEEE 519: 8% total and 5% for any single harmonic.

- Stage 4: unbalanced load flow. Put the house loads on single phases and check the voltage unbalance.

I’ll write each stage into the ETAP guide before you start it, the same way as Stage 1.

B. Act on what ETAP found

- Island overload. An evening island with every load on needs 18.6 kVA from an 18 kVA inverter. Run the same case in MATLAB and check whether the controller sheds load in time. If it doesn’t, either the shed rule or the inverter size has to change.

C. Real data (roadmap item 1, paused)

- Run run_real_days, which uses the real Sangli sun and real household loads.

- Add the bill numbers. The WCE campus bill is now in the repo, but the household bill is still pending.

D. Git housekeeping

- Open a pull request for real-data into master once step 5 passes the tests. After that, do etap-model into master.

- Delete the empty mg_hier\docs\etap\URJA_Microgrid folder and etap\URJA_Microgrid\_to_delete in Explorer.

E. After that (roadmap item 2)

- Build the ledger with real tariffs: ToD slots, net metering and prepaid P2P compared in Rs per house per month. The WCE bill helps here.

My suggestion is to start with A1 (short circuit). You already know ETAP now, and it answers the open protection question. All of this is saved in the progress report.