For Round 1, show what is real and verified: the two real node boards running live against MATLAB, plus the numbers that prove it.

Wiring the LEDs (same sketch on both boards)

Wire each LED as GPIO → 220–330 Ω resistor → LED long leg (+), with the short leg (−) to GND.

| LED | ESP32-WROOM pin | ESP32-S3 pin | On a load node (H1, H2, CL) | On the SB node (solar + battery) |
| --- | --- | --- | --- | --- |
| A (green) | GPIO 25 | GPIO 4 | Critical load ON | Battery discharging |
| B (yellow) | GPIO 26 | GPIO 5 | Flexible load ON | Battery charging |
| C (blue) | GPIO 27 | GPIO 6 | Blinks: lost the main controller | Blinks: lost the main controller |
| D (red) | GPIO 14 | GPIO 7 | Over-current trip or E-stop | Command clamped, battery fault or E-stop |
| E-stop (optional) | GPIO 33 → button → GND | GPIO 15 → button → GND | Opens both relays | Battery power to 0 |

The E-stop pin has an internal pull-up, so leaving it unconnected means "not pressed". Make WROOM = H1 and S3 = SB, so judges see one house and the battery.

Demo script (about 8 minutes)

1. Architecture (1 min). Use the diagram in the setup doc. The power system is simulated so outages can be tested safely; every controller and message is real. Each ESP is one component and makes its own safety decisions. The main controller makes the community decisions and only sees what the nodes report.

2. Live outage run (about 3 min). In hil/run_hil_nodes.m set PORTS = {'H1','COM14'; 'SB','COM16'} (your ports), SCEN = 'S11_demo_outage', PACE_S = 0.1, then run it.

| Time into the run | What to point at |
| --- | --- |
| 0–1 s | All LEDs off: the system starts with every switch off |
| ~1 s | H1 green and yellow on: the main controller enabled the loads |
| ~2–5 s | MATLAB prints ISLAND, then RESYNC, then GRID: it always syncs before closing the grid breaker |
| ~18 s | The grid fails. MATLAB prints ISLAND, the battery carries everything, and H1's critical load stays on |
| ~78 s | The grid returns. MATLAB prints RESYNC, then GRID, and closes the breaker within 5° |
| ~2.5 min | It ends with "Scenario rules: true" and "0 of 3000 differed" |

3. Safety is local (about 1.5 min). Set SCEN = 'S12_node_comms_loss' and PACE_S = 0.05, then run it. About 15 s in, H1's link is cut: its blue LED blinks and yellow goes off, but green stays on. "If the brain goes silent, the node protects itself and never cuts the critical load." The same happens on SB about 30 s in.

4. Proof (1 min). Show the numbers from mg_hier/results/results_summary.md:

- 13/13 scenarios pass

- 40/40 Monte Carlo runs pass, each with random faults and dropped links

- The C++ firmware matched MATLAB on 835,600 replies with 0 differences

- The real boards matched on 3,000 of 3,000 replies

Then show one figure, results/figures/S11_demo_outage.png.

5. What's next (30 s). "The Pi dashboard and AI layer are being connected now; the message format and access rules are already tested." Show the dashboard only if the Pi is live, otherwise skip it.

Before the judges arrive

- Do a dry run of steps 2 and 3. Close the Arduino Serial Monitor first, and type delete(serialportfind) in MATLAB if a port is stuck.

- Keep Plan B ready: mg_ac/hil/run_hil_demo.m with one board, already proven.

- Be honest if asked: the power hardware is simulated, two of the four nodes are real, and the Pi link is not yet live-tested.